## Sheet1
Regulator Data
Regulator ID: | 1
Line Segment: | 799 -701
Location: | 799
Phases: | A - B -C
Connection: | AB - CB
Monitoring Phase: | AB & CB
Bandwidth: | 2.0 volts
PT Ratio: | 40
Primary CT Rating: | 350
Compensator Settings: | Ph-AB | Ph-CB
R - Setting: | 1.5 | 1.5
X - Setting: | 3 | 3
Voltage Level: | 122 | 122