#### Distribution System Analysis Subcommittee

IEEE 4 Node Test Feeder

IEEE 4 Node Test Feeder

The system to be use in testing transformer models is shown in Figure 1:

Figure 1 – IEEE 4 Node Test Feeder

Both the primary line (Node1-Node 2) and the secondary line (Node 3-node4) will be constructed using the pole configuration shown in Figure 2.

Figure 2 – Pole Configuration

Phase Conductor:  336,400 26/7

GMR = 0.0244 ft.,  Resistance = 0.306 Ω/mile,  Diameter = 0.721 inch

Neutral Conductor:  4/0 6/1 ACSR

GMR = 0.00814 ft.,  Resistance = 0.492 Ω/mile,  Diameter = 0.563 inch

The source is a 12.47 kV line-to-line infinite bus.

Three-Phase Transformer Data:

| Connection | kVA | kVLL-high | kVLL-low | R - % | X - % |
| --- | --- | --- | --- | --- | --- |
| Step-Down | 6,000 | 12.47 | 4.16 | 1.0 | 6.0 |
| Step-Up | 6,000 | 12.47 | 24.9 | 1.0 | 6.0 |

Open Wye – Open Delta:

(Two Single Phase Transformers Each Rated)

| Connection | kVA | kV-high | kV-low | R - % | X - % |
| --- | --- | --- | --- | --- | --- |
| Step-Down | 2000 | 7.2 | 4.16 | 1.0 | 6.0 |
| Step-Up | 2000 | 7.2 | 24.9 | 1.0 | 6.0 |

Closed Connections Load Data:

|  | Balanced | Unbalanced |
| --- | --- | --- |
| # Phase-a |  |  |
| kW | 1800 | 1275 |
| Power Factor | 0.9 lag | 0.85 lag |
| # Phase-b |  |  |
| kW | 1800 | 1800 |
| Power Factor | 0.9 lag | 0.9 lag |
| # Phase-c |  |  |
| kW | 1800 | 2375 |
| Power Factor | 0.9 lag | 0.95 lag |

Open Connection Load Data:

|  | Balanced | Unbalanced |
| --- | --- | --- |
| # Phase-a |  |  |
| kW | 1200 | 850 |
| Power Factor | 0.9 lag | 0.85 lag |
| # Phase-b |  |  |
| kW | 1200 | 1200 |
| Power Factor | 0.9 lag | 0.9 lag |
| # Phase-c |  |  |
| kW | 1200 | 1583.33 |
| Power Factor | 0.9 lag | 0.95 lag |

### Line Impedances

4-wire configuration:

Phase impedance matrix:

Sequence impedances:

Three wire configuration:

Phase impedance matrix:

Sequence impedances:

Solutions